## Slide 1
SN2 bath center
The heat diffusion equation :
The thermal conductivity k :
The specific enthalpy H :
The specific heat capacity Cp :
The Dirac pulse :
Governing Equations
Abstract
Solid Nitrogen (SN2) can provide a uniform and stable cryogenic environment for High Temperature Superconducting (HTS) systems such as bulk samples during their magnetization and/or characterization. In this paper, we are studying a SN2 cooling system consisting of a cryocooler Sumitomo CH-110 and an exchanger in a Liquid Nitrogen (LN2) bath. In order to design this cooling system, an analytical model based on a nodal method coupled to a formulation of the thermal capacity (NMCTC) was realized. The model considers the thermal parameters variation as well as the phase change of the Nitrogen. In order to compare our results, we performed a 3D simulation on COMSOL Multiphysics. The performance of the cooling system was evaluated and we estimates that 50 L of LN2 can be cooled down to 20 K in 50 hours.
Design and Testing of a New Cooling System using Solid Nitrogen for Pulsed Field Magnetization and Characterization of HTS Bulks
Ghazi Hajiri1, Kévin Berger1 and Jean Lévêque1
1 – Groupe de Recherche en Energie Electrique de Nancy, University of Lorraine, France
Results
F-70 Indoor Water-Cooled Compressor
HiCube 300 Classic, DN 100 CF-F
Temperature sensor output
Cryo Diffusion
Pressure sensor
Cooling systems
Open cryostat view
CH-110 77K Cryocooler
Conclusion
The analytical model based on a nodal method coupled with a heat capacity formulation and the 3D simulation in COMSOL were validated with experimental measurements.
Pulsed field magnetization tests and characterization of HTS bulbs are planned soon.
T(K)
3D Simulation
Reality
Temperature sensor
Polystyrene support
SN2
Copper heat exchanger « CuC1 »